|  | ......................... pcs. .............................. € .............................. € GEZE Powerchain chain drive with IQ box Safety for protection of closing edges of power-operated windows in combination with safety edges and/or non-contact sensors For intelligent natural ventilation and use with vertically installed bottom-hung, top-hung and side-hung leaves, inward and outward opening, as well as for roof windows and skylights Chain drive as a direct opener in 24 V version The drive must be controlled via a micro-processor. The opening width and operating speed in ventilation mode can be programmed individually via software. The drive is equipped with electronic end position cut-off and overload protection and has electronically regulated soft start and soft stop. The activation is carried out via a GEZE emergency power control unit when smoke and heat extraction is needed. Synchronised multiple operation of up to 4 drives must be guaranteed without additional external module. Activation and setting of the synchro function is by means of an integrated DIP switch without additional programming being necessary Automatic switch-off when the end position is reached. Overload protection when opening and closing. Sealing via electronically defined pressure. Drive fixtures and chain attachments allow quick and easy installation from the front. For the protection of the main and secondary closing edges of power-operated windows in accordance with the Machinery Directive (protection class 4), IQ box Safety (TÜV-tested safety switching device) can be used in combination with safety edges and/or non-contact sensors. Technical data: Stroke: 600/800 and 1200 mm Tensile force/pressure: 600 N/max. 600 N, depending on stroke Voltage: 24 V DC / 230 V with external power supply Current consumption: Ventilation (24 V) 1.2 A IP rating: IP40 Ambient temperature: -5 °C to +70 °C Power supply cable: 2 m*, silicon sheathed * Special length on request Version: Solo ( ) Syncro ( ) Type of installation: ( ) surface-mounted Type of window: ( ) Bottom-hung leaf ( ) Top-hung leaf ( ) Side-hung leaf ( ) Roof window ( ) inward opening ( ) outward opening other types of leaf available on request Leaf dimensions: ........ mm width (min. 760 mm) ........ mm height (min. 400 mm, depending on the type of window, panel weight or leaf weight, stroke and type of installation) Leaf material: ( ) Wood ( ) Aluminium ( ) Plastic Opening width: ........ mm or max. ....... mm (to be completed by the bidder) Colour: ( ) EV1 ( ) white RAL 9016 ( ) according to RAL .......... Note: When used on bottom-hung leaves, we prescribe the use of separate safety scissors (2 pieces) for product liability reasons, e.g. GEZE safety scissors no. 35 or no. 60. Note: In order to guarantee the performance classes as set out in DIN EN 14351-1 with regard to wind load, sealing in the event of rain and air tightness, an additional locking mechanism must be planned on the window e.g. GEZE Power lock according to the specifications of the profile system manufacturer. Note: In accordance with Machinery Directive 2006/42/EC a risk assessment must be prepared for power-operated windows. The GEZE safety analysis for power-operated windows can serve as a guide for the risk analysis. These specifications determine the necessary protection class of the window and the definition of the protective measures. As the types of window and installation and the structural features of the buildings vary greatly, it is always advisable to undertake a feasibility study beforehand (especially in the case of retro-fitting). |
| --- | --- |
| 1.1 | ......................... pcs. .............................. € .............................. € ( ) Bracket set Powerchain type A (bottom-hung) ( ) Bracket set Powerchain type B (top-hung) |
| 1.2 | ......................... pcs. .............................. € .............................. € ( ) Safety scissors (2 pcs.) |
| 1.3 | ......................... pcs. .............................. € .............................. € ( ) Power lock locking drive |
| 1.4 | ......................... pcs. .............................. € .............................. € IQ box Safety for protection of closing edges of power-operated windows in combination with safety edges and/or non-contact sensors. (X) IQ box Safety (top hat rail casing) |
| 1.5 | .......... pcs. .................. € .................. € Surface-mounted casing For housing top hat rail power supplies or other electronic top hat rail components with maximum dimensions of approx. 119 x 93 x 55 mm. Aesthetic design. Technical data: Plastic casing white, cascading Cable guide surface mounting or flush mounting Version: Size W x H x D [mm]: approx. 193 x 130 x 82 |
| 1.6 | ......................... pcs. .............................. € .............................. € 24 V power supply ( ) Flush-mounted ( ) Top hat rail Note: You also need a 24 V power supply to supply the window drives as well as the IQ box Safety |
| 1.7 | ......................... pcs. .............................. € .............................. € Sensor technology for protection (optional position) Safety edges and/or non-contact sensors for protection of the main and secondary closing edges on the window. Definition of the protected window: ( ) Inward opening ( ) Outward opening ( ) Bottom-hung window ( ) Top-hung window ( ) Side-hung window ( ) Parallel-opening vent window other types of leaf available on request …………mm width …………mm height …………mm installation height …………mm opening width Sensors ( ) Non-contact sensor ( ) Safety edge |
| 1.8 | ......................... pcs. .............................. € .............................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
| 1.9 | ......................... pcs. .............................. € .............................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
| 1.11 | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing – 2-year guarantee Maintenance and testing of hold-open systems (optional position) Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
| 1.12 | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package Service maintenance – 3-year guarantee Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
| 1.13 | ......................... pcs. .............................. € .............................. € Service maintenance - exclusive package Service maintenance – 5-year guarantee Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 60 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 5 years |
| 1.14 | ......................... pcs. .............................. € .............................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |